Model 5100ALBV COLLECTanDRAIN

2.1 SPRINKLER SPECIALTY PIPE FITTINGS

* + - * 1. Auxiliary Drain and Condensation Collecting Assemblies for Dry Pipe and Preaction Sprinkler Systems:

Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; Model 5100ALBV COLLECTanDRAIN™.

<**Insert manufacturer's name**>.

Standards:

NFPA 13 and NFPA 25.

Components:

1 inch MIPT x FIPT Brass quarter turn ball valve with chrome plated ball.

1 inch MIPT x FIPT Ball Valve with Side Ports.

Water Detection Alarm with Brass Nipple.

Powered by a 9-volt battery to operate a red LED visual indicator and an over 92 dB beeping alarm which are activated when water is present in the COLLECTanDRAIN™.

Battery operated system provides multiple years of service for intermittent alarming or can operate continuously for 72 hours. Unit will provide low battery power indication through audible chirp and yellow LED visual indicator.

Device may be optionally hardwired to a 12 to 24 VDC power source.

Unit features a test button to confirm operational integrity, offers left or right side installation, and can be isolated for service or battery replacement.

Unit may be configured to alarm only when temperature is below 45°F or at any temperature.

Device may be wired to provide remote notification with NO and NC terminals.